## Rainwater
mastermep.com ↗
Roof rainwater flow
STEP 1 / 2 · MasterMEP · Calculate the rainwater flow from the roof |  |  |  |  | Step 2 →
TOTAL FLOW |  | AREA CHECK
30 |  | ✓ Areas match
litres / second (L/s) |  | Defined 600 m² · Target 600 m²
Input cell | Automatic | Fill in the yellow cells first; results update automatically.
1 Enter rainfall and target area
Rainfall intensity | 180 | Design rainfall for the project location. 180 is a training example only.
Rainfall unit | mm/h | Which unit did you use for rainfall? mm/h or L/s/m²
Target effective area | 600 | Must equal the sum of the catchment areas below.
PROJECT INFO (optional)
Station / location | Training example; enter local data |  | e.g. meteorological station / city
Duration / return period | Enter per project |  | e.g. 5 minutes / once in 5 years
Rainfall source / date | Training example; enter local data |  | Rainfall data, report and date
2 Divide the roof into catchments
Catchment = roof area draining to the same outlet (or outlet group). Enter the area in each row and select the roof type; C and flow are calculated automatically.
Unit rainfall flow (r) | 0.05 | Automatic. If mm/h is selected, r = rainfall ÷ 3600.
Catchment | Effective area (m²) | Roof type (select from list) | Manual C (“Other” only) | C (automatic) | Flow (L/s)
Catchment 1 | 150 | Membrane roof (slope ≤3°) |  | 1 | 7.5
Catchment 2 | 150 | Membrane roof (slope ≤3°) |  | 1 | 7.5
Catchment 3 | 150 | Membrane roof (slope ≤3°) |  | 1 | 7.5
Catchment 4 | 150 | Membrane roof (slope ≤3°) |  | 1 | 7.5
Catchment 5
Catchment 6
Catchment 7
Catchment 8
Total | 600 |  |  |  | 30
Reminders
• 180 mm/h and 600 m² are training examples; replace them with your own project data.
• Calculation: Q = r × A × C (flow = unit rainfall × effective area × runoff coefficient).
• This value is the primary drainage flow. Emergency overflow, pipe and outlet capacity are checked separately.
• For the method, roof coefficients and sources, see the Info sheet. |  |  |  |  | Info →

## Downpipe sizing
mastermep.com ↗
Pipe and downpipe sizing
STEP 2 / 2 · MasterMEP · Gravity system · preliminary sizing |  |  |  |  | ← Step 1
DOWNPIPES INCL. OUTLET CAPACITY |  | MIN. QTY BY PIPE ONLY |  | DEFINED CATCHMENTS
16 |  | 4 |  | 4
pcs · incl. outlet capacity |  | pcs · based on pipe capacity only |  | catchments
Input cell | Automatic | Fill in the yellow cells; everything else is calculated automatically.
1 Select pipe and roof outlet
Calculation mode | Standard | Standard: preset assumptions. Expert: your own f and kb values (bottom of sheet).
Inner diameter | 100 | REAL INNER DIAMETER of the pipe you plan to use (not outer diameter).
Pipe capacity | 10.7114 | Flow a SINGLE downpipe of the selected diameter can carry.
Outlet info | Enter model, source and water head (mm) |  | Optional note (for the report)
2 Review catchment results
In the yellow column, enter the capacity (L/s) given in the manufacturer datasheet of your selected outlet for the water head allowed in the project. All diameters are INNER diameters.
Catchment | Flow (L/s) | Outlet capacity (L/s) · datasheet | Min. inner dia. per downpipe (mm) | Min. qty by pipe | Min. qty with outlet
Catchment 1 | 7.5 | 2 | 90 | 1 | 4
Catchment 2 | 7.5 | 2 | 90 | 1 | 4
Catchment 3 | 7.5 | 2 | 90 | 1 | 4
Catchment 4 | 7.5 | 2 | 90 | 1 | 4
Catchment 5
Catchment 6
Catchment 7
Catchment 8
3 Pipe capacity table (single downpipe, by inner diameter)
The selected diameter is highlighted. Capacities use the f and kb values in Advanced settings below.
Inner dia. (mm) | Capacity (L/s)
75 | 4.9732
90 | 8.0874
100 | 10.7114
110 | 13.8115
125 | 19.4225
150 | 31.5851
160 | 37.5176
200 | 68.0289
250 | 123.3539
300 | 200.5992
Advanced settings (optional)
No need to change anything here in Standard mode. If you select “Expert”, fill in the yellow fields and the basis.
Parameter | Filling ratio f | Roughness kb (mm)
Values in use | 0.33 | 0.25 | Automatic: chosen by your mode.
Expert value |  |  | f: 0.20 – 0.33 · kb: greater than 0
Basis / source
• f: water-filled share of the cross-section (not water depth / pipe diameter). A smaller f reduces capacity.
• kb: hydraulic roughness in mm. A larger kb reduces capacity; it is not selected from the roof type.
Reminders
• Valid only for circular, straight, gravity-driven vertical downpipes. Not a siphonic or horizontal pipe calculation.
• Quantities assume the flow is shared equally within the catchment and ONE roof outlet is connected to EACH downpipe.
• Emergency overflow, blockage safety, unbalanced flow, gutters and downstream lines are checked separately; not included in the quantity.
• For the capacity formula, assumptions and sources, see the Info sheet. |  |  |  |  | Info →

## Info
mastermep.com ↗
Info and sources
Runoff coefficients · calculation method · assumptions · sources
Roof type and runoff coefficient (C)
Roof type | C
Membrane roof (slope ≤3°) | 1
Metal / glass / fibre-cement (slope ≤3°) | 1
Gravel roof (slope ≤3°) | 0.8
Extensive green roof (<10 cm, slope ≤5°) | 0.5
Extensive green roof (≥10 cm, slope ≤5°) | 0.4
Intensive green roof (≥30 cm, slope ≤5°) | 0.2
Extensive green roof (slope >5°) | 0.7
Other / manufacturer data (manual C) | enter manually
• For tile and other roof types, a documented project / manufacturer C value is required; no default value is assumed.
• Reduced C values are not an emergency overflow calculation. Verify the design standard accepted for the project.
• Coefficient source: LORO, Runoff Coefficient (DIN 1986-100 peak value examples), accessed 29 Oct 2026. Use only if the listed conditions and the project basis apply.
How is the rainwater flow calculated?
• Q = r × A × C → flow (L/s) = unit rainfall flow × effective area × runoff coefficient.
• r (L/s/m²): if mm/h is selected, r = rainfall ÷ 3600; if L/s/m² is selected, r = the rainfall value itself. (1 mm × 1 m² = 1 L; 1 hour = 3600 s)
• Catchment = roof area draining to the same outlet (or outlet group). Enter the area for each catchment and select the roof type.
• If “Other / manufacturer data” is selected, enter C manually. If any catchment data is missing, the total shows “Missing input”.
• Example: 4 × 150 m² → 4 × 7.50 = 30.00 L/s. 100 / 100 / 100 / 300 m² → 5 / 5 / 5 / 15 L/s.
• The target-area difference must be zero; this check does not mean hydraulic adequacy.
• The result is the primary drainage flow. Emergency overflow, pipe and outlet capacity are calculated separately.
How are pipes and downpipes sized?
• Pipe capacity: Qp = 2.5 × 10^-4 × kb^-0.167 × di^2.667 × f^1.667 (Qp: L/s; kb and di: mm).
• di: inner diameter · f: water-filled share of the cross-section (not water depth / pipe diameter) · kb: hydraulic roughness (not selected from the roof type).
• A smaller f or a larger kb reduces capacity.
• Standard mode: f = 0.33 and kb = 0.25 mm (preliminary sizing assumptions of the reference method). Verify suitability for your project.
• Expert mode requires a documented project basis; f must be between 0.20 and 0.33.
• Valid only for circular, straight, gravity-driven vertical downpipes. Not a siphonic system or horizontal pipe calculation.
• “Min. inner diameter for one downpipe” is the first sufficient diameter in the list; above 300 mm a separate sizing is required.
• Quantities assume the flow is shared equally within the catchment and ONE roof outlet is connected to EACH downpipe.
• Outlet capacity: enter the value (L/s) given in the manufacturer datasheet for the water head allowed in the project.
• If no outlet data is entered, only a lower bound based on pipe capacity is found; the total with outlets is not shown.
• Unbalanced flow, connections, ponding, gutters, bends and downstream lines are checked separately.
• Emergency overflow and blockage safety are designed separately; they are not included in the quantity given.
• Select a real product that provides the resulting inner diameter. Do not reduce the diameter required by the outlet connection.
Sources
• MasterMEP calculation method and training example
https://mastermep.com/yazi?slug=cati-yagmur-suyu-debisi
• Turkish State Meteorological Service (MGM) short-duration rainfall data (design intensity is not selected automatically)
https://www.mgm.gov.tr/veridegerlendirme/maksimum-yagislar.aspx
• LORO – Runoff Coefficient (roof coefficients)
https://www.loro.de/en/service/abc/runoff-coefficient
• HR Wallingford, R W P May, SR620 (2003), §10.1.1, Equation 10.1, p.34
https://eprints.hrwallingford.com/495/1/Manual-roof-drainage-system-HRWallingford-SR620.pdf
• The HR Wallingford guide describes the BS EN 12056-3:2000 method (historical source). Verify project requirements and current product data.